## Summary (2)
[18 empty] | DATE | 31.08.2021
SR. NO. | Space Description | Area To be Airconditioned | Total Height | False Ceiling Height | Fresh Air | Occupancy | Electrical Load |  | As per Heatload |  | SHF | ADP | PROPOSED INDOOR UNITS
|  | (Sq.Ft) | (FT) | (FT) | CFM | Nos. | Lighting Load | Eqpt. Load | TR | CFM |  |  | IDU MODEL | TYPE | TR | CFM | QTY. | TOTAL TR | TOTAL CFM
[7 empty] | Watts | Kw
SYSTEM 1
1 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | vcc 16 | compact cassette | 1.3 |  | 1 | 1.3
2 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | dsd 72 | ducted | 6 |  | 1 | 6
3 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | vcc 10 | compact cassette | 0.8 |  | 1 | 0.8
4 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | vcc 10 | compact cassette | 0.8 |  | 1 | 0.8
5 | #REF! | #REF! | #REF! | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | vlc 12 | large cassette | 1 |  | 1 | 1
7 | #REF! | #REF! | #REF! | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | vhw16b | hiwall | 1.3 |  | 1 | 1.3
11.2
Assumtion | [16 empty] | ODU (HP) | 12 | 0
1 | Inside Condition : 24 Deg C + / -1 Deg F | [15 empty] | ODU (TR) | 9.6
| RH - Around 55% | [13 empty] | 0 |  | DIVERSITY | 1.1667
2 | Out Side Condition : 35 Deg C | [13 empty] | 0
3 | Lighting Load - 1.0 Watts / Sq.ft | [10 empty] | 215.3846 | 2.6
4 | Fresh Air - 1 Air change or 7.5cfm per person whichever is higher | [14 empty] | 12 | HP
5 | Equipment Load Considered 150watts / PC. | [14 empty] | 9.6 | TR
6 | Occupancy consider as per Architectural layout | [14 empty] | 116.7% | Diversity
7 | Exposed Glass Double Pane inside ventian blind or Roller Shade. | [12 empty] | Factor 1 | 0.99 | 9.409 | Derated ODU TR
8 | Floor below is considered AC/non-ACnd Floor above is exposed. | [12 empty] | Factor 2 | 0.99 | 9.6 | Total Nominal IDU TR
9 | Exposed Roof is insulated with 50mm Thermocol/Equivalant Material. | [14 empty] | 0.9801 | IDU Performance factor
[16 empty] | 9.409 | IDU Capacity @ diversity
[16 empty] | 0 | Total IDU TR as per heatload
Result
Note - Factor 1 needs to be change as per indoor WBT.
Note - Factor 2 needs to be change as per Equvivalent Piping Length & Elevation difference

## M.BED 1
HEAT LOAD ESTIMATE FOR UNNIKRISHNANS VILLA
| FIRST FLOOR - DISCUSSION AREA | [7 empty] | R0
CUSTOMER : |  | M.BED 1 |  |  | DESIGN CONDITIONS
ESTIMATED BY : |  | RONY RUFUS |  | TIME OF PEAK LOAD: |  |  | APRIL, 16:00 HRS
DATE : |  | 2024-08-22 |  |  | DB | % RH | WB | TH | GR/LB
AREA | = | 204.8699 | SQFT | OUTSIDE | 92 | 59 | 79.74 | 43.27 | 134.7
TOTAL HT | = | 10 | FEET | INSIDE | 74 | 55 | 63.84 | 29.14 | 69.1
FC LVL | = | 10 | FEET | DIFF. | 18 | X | X | 14.13 | 65.6
PEOPLE : | 3 | NOS. X | 7.5 | CFM = | 34.7922 |  | Correction Factor for walls |  | 5
1 | AIR CHANGES PER HOUR |  |  | = | 34.145
FRESH AIR |  |  |  | = | 34.7922
STRUCT. | SQFT | FACTOR | TEMP. | BTU/HR | EFFECTIVE ROOM LATENT HEAT | [5 empty] | 1.408
EFFECTIVE ROOM SENSIBLE HEAT |  |  |  |  | F. A. | 34.7922 | 65.6 | 0.15x0.67 | 229.378
WALL N |  | 0.34 | 9 | 0 | PEOPLE | 3 | NOS. | 205 | 615
WALL NE | 196.54 | 0.34 | 15 | 1002.354 | ERLH SUBTOTAL |  |  |  | 844.378
WALL E |  | 0.34 | 23 | 0 | FACTOR |  |  | 5% | 42.2189
WALL SE | 159.74 | 0.34 | 23 | 1249.1668 | ERLH TOTAL |  |  |  | 886.5969
WALL S |  | 0.34 | 21 | 0 | 1) EFFECTIVE ROOM TOTAL HEAT |  |  |  | 13711.5233
WALL SW | 164.43 | 0.34 | 19 | 1062.2178 | 2) F. A. | 34.7922 | 14.13 | 4.5x0.85 | 1880.4222
WALL W |  | 0.34 | 17 | 0 | GRAND TOTAL HEAT SUBTOTAL = 1 + 2 + 3 |  |  |  | 15591.9455
WALL NW | 117.1 | 0.34 | 11 | 437.954 | FACTOR |  |  | 3% | 467.7584
GLASS N | 0 | 0.56 | 11 | 0 | GRAND TOTAL HEAT |  |  |  | 16059.7039
GLASS NE | 0 | 0.56 | 11 | 0 | AIRCONDITIONING TONNAGE |  |  |  | 1.3383
GLASS E | 0 | 0.56 | 11 | 0
GLASS SE | 0 | 0.56 | 11 | 0 | ERSHF |  |  |  | 0.93534
GLASS S | 0 | 0.56 | 11 | 0 | INDICATED ADP |  |  |  | 55
GLASS SW | 12 | 0.56 | 113 | 759.36 | SELECTED ADP |  |  |  | 55
GLASS W | 0 | 0.56 | 165 | 0 | DEHUMIDIFIER CFM |  |  |  | 735.2899 | 1.8382
GLASS NW | 29.5 | 0.56 | 118 | 1949.36
ALL GLASS | 41.5 | 1.13 | 18 | 844.11 | RETURN AIR GAIN
PRT. WL. | 356.28 | 0.4 | 13 | 1852.656 | STRUCT. | SQFT | FACTOR | TEMP. | BTU/HR
PRT. GLS. | 0 | 1.13 | 13 | 0 | WALL N | 0 | 0.34 | 7 | 0
ROOF | 0 | 0.48 | 38 | 0 | WALL NE | 0 | 0.34 | 13 | 0
CEILING | 204.8699 | 0.4 | 13 | 1065.3232 | WALL E | 0 | 0.34 | 21 | 0
FLOOR | 0 | 0.4 | 13 | 0 | WALL SE | 0 | 0.34 | 21 | 0
F. A. | 1 | 18 | 0.15x1.08 | 2.916 | WALL S | 0 | 0.34 | 19 | 0
PEOPLE | 3 | NOS. | 245 | 735 | WALL SW | 0 | 0.34 | 17 | 0
LIGHT (w) | 1 | 204.8699 | 3.41 | 698.6062 | WALL W | 0 | 0.34 | 15 | 0
EQPT. (kw) | 0 | 1 | 3410 | 0 | WALL NW | 0 | 0.34 | 9 | 0
OTHER (kw) | 0 | 1 | 3410 | 0 | PRT. WL. | 0 | 0.4 | 13 | 0
ERSH SUBTOTAL |  |  |  | 11659.024 | 3) TOTAL R.A. GAIN |  |  |  | 0
FACTOR |  |  | 10% | 1165.9024
ERSH TOTAL |  |  |  | 12824.9264

## M.BED 2
HEAT LOAD ESTIMATE FOR UNNIKRISHNANS VILLA
| FIRST FLOOR - DISCUSSION AREA | [7 empty] | R0
CUSTOMER : |  | M.BED 1 |  |  | DESIGN CONDITIONS
ESTIMATED BY : |  | RONY RUFUS |  | TIME OF PEAK LOAD: |  |  | APRIL, 16:00 HRS
DATE : |  | 2024-08-22 |  |  | DB | % RH | WB | TH | GR/LB
AREA | = | 170.8416 | SQFT | OUTSIDE | 92 | 59 | 79.74 | 43.27 | 134.7
TOTAL HT | = | 10 | FEET | INSIDE | 74 | 55 | 63.84 | 29.14 | 69.1
FC LVL | = | 10 | FEET | DIFF. | 18 | X | X | 14.13 | 65.6
PEOPLE : | 3 | NOS. X | 7.5 | CFM = | 32.7505 |  | Correction Factor for walls |  | 5
1 | AIR CHANGES PER HOUR |  |  | = | 28.4736
FRESH AIR |  |  |  | = | 32.7505
STRUCT. | SQFT | FACTOR | TEMP. | BTU/HR | EFFECTIVE ROOM LATENT HEAT | [5 empty] | 1.408
EFFECTIVE ROOM SENSIBLE HEAT |  |  |  |  | F. A. | 32.7505 | 65.6 | 0.15x0.67 | 215.9175
WALL N |  | 0.34 | 9 | 0 | PEOPLE | 3 | NOS. | 205 | 615
WALL NE | 196.54 | 0.34 | 15 | 1002.354 | ERLH SUBTOTAL |  |  |  | 830.9175
WALL E |  | 0.34 | 23 | 0 | FACTOR |  |  | 5% | 41.5459
WALL SE | 159.74 | 0.34 | 23 | 1249.1668 | ERLH TOTAL |  |  |  | 872.4633
WALL S |  | 0.34 | 21 | 0 | 1) EFFECTIVE ROOM TOTAL HEAT |  |  |  | 13569.7496
WALL SW | 164.43 | 0.34 | 19 | 1062.2178 | 2) F. A. | 32.7505 | 14.13 | 4.5x0.85 | 1770.0741
WALL W |  | 0.34 | 17 | 0 | GRAND TOTAL HEAT SUBTOTAL = 1 + 2 + 3 |  |  |  | 15339.8237
WALL NW | 117.1 | 0.34 | 11 | 437.954 | FACTOR |  |  | 3% | 460.1947
GLASS N | 0 | 0.56 | 11 | 0 | GRAND TOTAL HEAT |  |  |  | 15800.0184
GLASS NE | 0 | 0.56 | 11 | 0 | AIRCONDITIONING TONNAGE |  |  |  | 1.3167
GLASS E | 0 | 0.56 | 11 | 0
GLASS SE | 0 | 0.56 | 11 | 0 | ERSHF |  |  |  | 0.93571
GLASS S | 0 | 0.56 | 11 | 0 | INDICATED ADP |  |  |  | 55
GLASS SW | 12 | 0.56 | 113 | 759.36 | SELECTED ADP |  |  |  | 55
GLASS W | 0 | 0.56 | 165 | 0 | DEHUMIDIFIER CFM |  |  |  | 727.9719 | 1.8199
GLASS NW | 29.5 | 0.56 | 118 | 1949.36
ALL GLASS | 41.5 | 1.13 | 18 | 844.11 | RETURN AIR GAIN
PRT. WL. | 356.28 | 0.4 | 13 | 1852.656 | STRUCT. | SQFT | FACTOR | TEMP. | BTU/HR
PRT. GLS. | 0 | 1.13 | 13 | 0 | WALL N | 0 | 0.34 | 7 | 0
ROOF | 0 | 0.48 | 38 | 0 | WALL NE | 0 | 0.34 | 13 | 0
CEILING | 204.8699 | 0.4 | 13 | 1065.3232 | WALL E | 0 | 0.34 | 21 | 0
FLOOR | 0 | 0.4 | 13 | 0 | WALL SE | 0 | 0.34 | 21 | 0
F. A. | 1 | 18 | 0.15x1.08 | 2.916 | WALL S | 0 | 0.34 | 19 | 0
PEOPLE | 3 | NOS. | 245 | 735 | WALL SW | 0 | 0.34 | 17 | 0
LIGHT (w) | 1 | 170.8416 | 3.41 | 582.5697 | WALL W | 0 | 0.34 | 15 | 0
EQPT. (kw) | 0 | 1 | 3410 | 0 | WALL NW | 0 | 0.34 | 9 | 0
OTHER (kw) | 0 | 1 | 3410 | 0 | PRT. WL. | 0 | 0.4 | 13 | 0
ERSH SUBTOTAL |  |  |  | 11542.9875 | 3) TOTAL R.A. GAIN |  |  |  | 0
FACTOR |  |  | 10% | 1154.2988
ERSH TOTAL |  |  |  | 12697.2863